PART 1- GENERAL

  - DESCRIPTION OF WORK

- Extent of Perimeter Security Lighting work is indicated by drawings and schedules

- Type of Perimeter Lighting in this section include the following:

Low Voltage LED Fence Mounted and Wall Mounted Perimeter Security Lights, low voltage power supply and wire direct burial, attached directly to existing or new fence system, or wall or conduit mounted, as indicated below and in accompanying design documents.

- Perimeter Security Lighting may be integrated and activated using hard signal wire or radio with multiple intrusion detection third party system(s). Contractor shall insure compatibility and operation with third party system(s)

PART 2 PRODUCTS

2.01 ACCEPTABLE MANUFACTURERS:

A. 	Manufacturer: Subject to compliance with requirements, provide products of manufacturers listed on the drawings within the lighting fixture schedule.

2.02 PERIMETER FENCE MOUNTED SECURITY LIGHTING FIXTURES:

- General: Provide lighting fixtures, of size, wattage, lumen output, optical pattern, ratings, and 3rd party LM79 testing documentation as indicated; complete with, but not necessarily limited to housings, drivers, power supplies and wiring as per quantity and design and luminaire model specified on plans.

2.03 LUMINAIRES:

- Fence mounted luminaires shall be Cast Perimeter Lighting Generation 3 Model # CPL38, CPL312, CPL316, or CPL325 series. Dimensions: 29” (73.cm) High, with a top luminaire assembly 6.0”  ( 15.0cm) Wide , 9.00” ( 23.0cm) long, 1.375”(3.25cm) thick. Standard luminaire stem length is 24” inches: (61 cm) and can be customized by adding a dash at the end of the model number indicating the desired pipe length by the inch up to a maximum of 36” inches or (92cm). Castings shall be constructed of die cast aluminum alloy together with sand blasted matte finish schedule 40 aluminum 6061-T6 pipe. Luminaire shall have machined brass ball joint style swivel adjustment knuckle to allow installer seamless 0°to 22° adjustment of luminaire head off 90° in any orientation to allow optical pattern adjustment to accommodate grade, surface or field adjustment required by end user. Luminaire shall allow full 360°rotation of the fixture head. Luminaire shall mount directly to the round upright fence post ranging from 1-1/4” to 4.5” OD using standard Luminaire mounting bracket supplied with CPL3 Series fixture. Luminaire shall also accommodate 6”x6” square fence post using optional mounting bracket model# CPL3MB6X6 and 6” Round upright fence posts using optional mounting bracket model# CPL3MB6R purchased separately. Luminaire shall be provided with a separate back mounting plate and “U” bracket that detaches from luminaire base and mounts easily to the upright round fence post.  Luminaire shall attach to back mounting plate by way of three ¼-20 304 stainless pan head screws. Fixture mounting plate shall attach to upright fence post using 5-16 x 6” long U bracket style 304 stainless steel 5/16-18 UNC threaded end connection together with nut and washer hardware. Luminaire base shall mount against back mounting plate bracket and provide two “mouse hole” style one person quick connect attachment. (See below figure # 13 for complete mounting instructions) Base electrical wiring Junction box inside dimension 2.5” (6.5cm) Depth x 2.5” (6.5 cm) Height x 4.50” (11.5cm) Width with removable front wiring compartment cover plate and upper housing molded drip edge feature, together with bottom drop down wire strain relief compression plate, to accommodate the wire feeding and exiting luminaire. Bottom drop down wire strain relief plate shall accept # 14-2, # 12-2 and # 10-2 SPT style No-Ox wire. Bottom plate shall include standard ½” (.860”) knock-out electrical fitting access with plastic removable plug.   Luminaire shall be provided with Tyco “Mate-N-Lock” commercial pin and socket connector model #770069-1 & 770065-1 to allow the coupling or decoupling of power source to luminaire. Driver Circuit (s) shall be easily replaceable using same Tyco Connectors and held in place by thermally conductive Copper Bar Stock retainer and set screw. Ambient operating range shall be from -40°C to +55°C. Low voltage operating input range shall allow for between 12 to 30 volts power. For Optimal operation power luminaires at between 26 and 17 Volts DC Power.  Luminaire shall consume the following wattage and deliver the following lumens when operating on DC power as follows:

  - CPL38   DC Power, 10.72 Watts consumed at 26-17V DC Delivering 1,172 Lumens

  - CPL312 DC Power, 17.56 Watts consumed at 26-17V DC Delivering 1,662 Lumens

  - CPL316 DC Power, 21.75 Watts consumed at 26-17V DC Delivering 2,229 Lumens

  - CPL325 DC Power, 33.05 Watts consumed at 26-17V DC Delivering 3,064 Lumens

Drive circuit power factor shall be .86 or better. Thermal management shall be passive thermal transfer through components in physical contact with thermal pads and luminaire housing.  Thermal pad shall be .010” thick to bond aluminum LED board to the fixture body. No thermal grease shall be allowed for thermal bonding of LED’s.  Unit shall not exceed an LED junction temperature test of 75°C when run for two hours at @24.0V AC, 25.8 Watts, Power Factor .86, at a room temperature of 24°C .

Luminaire models shall deliver from the fixture the following lumen values when operating between 17-26V DC :

  - CPL38  	At 17-26V DC 	1172 lumens

  - CPL312 	At 17-26V DC	1662 Lumens

  - CPL316 	At 17-26V DC	2229 Lumens

  - CPL325 	At 17-26V DC	3064 Lumens

NOTE: Ideal operation range of Luminaires is between 17V to 26V DC power

Drive Circuit components shall not incorporate the use of any aluminum electrolytic capacitor components. Surge & Spike Protection shall suppress both transient spikes and surges over 40 Volts. Drive circuit shall be moisture protected and fully encapsulated in thermally conductive potting material. Four LED array Shall be housed in optics manufactured of PMMA 8N Plexiglas high impact clear custom with precision 360 degree coverage and beam angle of 154° model # XCPO54 together with two-sided moisture resistant adhesive tape secured between optic and PCB provided with center optic screw. PCB and optic array shall be mounted using stainless 10-24 screws. Optic array shall be further sealed around circumference using self-leveling RTV silicone forming a moisture resistant bond between the optic, fixture casting, thermal pad, and PCB. LED’s shall be manufactured by Cree XPG-2 series BWT-01-0000-00000KE4, 4500 Kelvin +- 250K, CRI index of 70, Lumen maintenance L-70 of 63,500 hours and manufactured with conformal coating placed over the solder pads. Luminaire driver shall be tested by an independent laboratory to FCC standards and comply for both electromagnetic Interference of Class B conducted and radiated emissions. Luminaire shall be tested to UL electrical standard for safety   1838 & 8750; CE listed and certified to Canada and US Standards C22.2 No.250.0 & C22.2 No.250.13. Luminaire shall be suitable for wet locations. Luminaire shall be RoHs compliant. Luminaire shall meet or exceed IESNA Cut-off Classification; Full cut off (0% above nadir) and dark sky compliant (MLO) for reduction of light pollution and light trespass. Luminaire shall have a maximum BUG rating of B2-U1-G1. Luminaire shall have full accredited NVLAP LM-79 third party validation report available using IESNA LM79: 2008 Approved Methods for Electrical and Photometric Measurements of Solid-State Lighting Products and ANSI NEMA ANSLG C78.377: 2008 Specification of the Chromaticity of Solid-State Lighting Products.   As manufactured by Cast   Lighting 1120- Goffle Road, Hawthorne NJ 07506 or approved equal.

- Should CPL3 Series perimeter security light require mounting mid-way up the fence post not attaching to the topmost section, contractor shall use model # CPL3FSB standoff bracket to prevent luminaire top from hitting fence post and allow obstruction free level alignment of the reflector section of the luminaire.

2.04 LUX DISTRIBUTION:

Typical fixtures installed twenty feet on center (6.096 meters) mounted on a ten-foot fence (3.03 meter) placing the luminaire head at twelve feet off grade (3.63 meters) shall deliver the following average Lux level at 30 feet (9.14 Meter) from the inside and outside of fence and along the fence line operating at between 17V DC and 24V DC as follows:

Minimum Lux Along Fence Line		Minimum Lux at 30 Feet (9.14 meter) From Fence line

- CPL38	7.89 Lux (*)				3.49 Lux (**)

- CPL312	11.34 Lux (*)				4.66 Lux (**)

- CPL316	19.12 Lux (*)				5.37 Lux (**)

- CPL325	25.87 Lux (*)				7.52 Lux (**)

- (*) Value provided along fence line between 2nd to last and last fixture.

- (**) Value provided at 30 feet from fence line between 2nd to last and last fixture.

- NOTE: Above LUX values increase slightly as the saturation of light overlap increase along the fence line.

- Please reference LUX Plot information on web site that provide different mounting heights and fixture spacing for precise lux distribution. www.cast-lighting.com – engineering library section of web site. AGI32 Plot Files also available.

2.05 EXTERIOR PERIMETER LIGHTING CONTROL AS DIRECTED BY OWNER.

A. 	Power Supply Dawn to Dusk Days of the Week Control: Power supply shall come equipped with manual on off control, integral dawn to dusk control feature. Power supply shall provide eight-hour delay on, and delay off, along with GPS astronomical time clock control feature with days of the week on off control. Model CPT600DCA 600Watt and CPT1200DCA 1200 Watt, As manufactured by Cast Lighting 1120- Goffle Road, Hawthorne NJ 07506 or approved equal.

- Power Supply Dawn to Dusk, Days of the Week, Third Party Activation: Power supply shall come equipped with manual on off control and integral dawn to dusk control feature. Power supply shall provide eight-hour delay on, and delay off, along with GPS astronomical time clock control feature with days of the week on off control. The power supply shall provide a third-party dry contact activation feature. Third Party Dry Contact Activation Feature can operate lighting system in one of four typical settings once activated by a NO or NC signal wire or optional radio control provided by third party intrusion detection system such as a microwave, motion, laser, camera analytics, and other intrusion detection or third-party system(s). Features shall include:

  - Dawn to Dusk, Days of the Week lighting control.

  - Dark until NO or NC activation signal is sent with user set on duration from one minute to twelve hours of operation.

  - User set control of security lights for two activity monitored zones outside the perimeter fence. The two monitored zones are referenced as Pre alarm and Alarm zones and require two independent signal wires to power supply for each zone. Furthest zone from fence is referred to as the pre alarm zone and the second zone closest to fence is referred to as the alarm zone. Both pre alarm and alarm zone allow for user set lighting flash on time, Light flash off time and duration of flashing control. In addition to flash on off duration settings user can set Lights on after flash feature, with the run time set by user. This feature provides constant light of the activated zone area to provide security personnel an illuminated setting devoid of flashing lights. Activation of both pre alarm and alarm is performed using dry contact NO or NC signal wire or optional industrial radio signal sent by a third-party intrusion detection system.

    - Lighting System Power Supply shall allow operation of lighting system after receiving a third-party NO or NC signal from pre-alarm and alarm zone for a user set duration ranging from one minute to twelve hours of operation.

    - Lighting System Power Supply shall allow custom on flash and off flash settings from one to sixty seconds for both Pre alarm and alarm settings for a user set time from one to twelve hours.

    - Lighting System Power Supply Systems shall override pre alarm light program and activate alarm program once alarm zone signal is sent to power supply.

    - Lighting System Power Supply System shall provide a light on after flash setting once the flash sequence program has concluded for both pre alarm and alarm setting for a user defined time from one minute to twelve hours. This feature provides security guards the lighting required to inspect area of attempted breach.

    - Model CPT1200DCAI. 1200 Watt As manufactured by Cast Lighting 1120- Goffle Road, Hawthorne NJ 07506 or approved equal.

Power Supply Dawn to Dusk Days of the Week Control: Power supply shall come equipped with manual on off control, integral dawn to dusk control feature. Power supply shall provide eight-hour delay on, and delay off, along with GPS astronomical time clock control feature with days of the week on off control. Model CPT600DCA 600Watt and CPT1200DCA 1200 Watt, As manufactured by Cast Lighting 1120- Goffle Road, Hawthorne NJ 07506 or approved equal.

  - LOW VOLTAGE POWER SUPPLY.

- SYSTEM POWER SUPPLY: Low Voltage Direct Current power supply shall be available in 600 watt and 1200watt capacity provided in an outdoor rated enclosure convection vented with internal cooling fan with intake bug screen venting, 304 stainless-steel weatherproof cabinet. Power Supply shall operate on any of the following primary alternating current voltages, 115V, 120V, 208V, 230V, 240V and 277V and European 220V/240V, and operate between 47 to 63 Hertz (HZ). Power supply shall operate from 100V AC to 277V AC.  Secondary taps shall deliver 26V DC Constant voltage under any secondary load condition or primary power supply voltage from 100V AC to 277V AC. Primary amps shall range per 600 watts from 7Amps / 115VAC, 3.3A / 230VAC , 2.9A / 277VAC. For 1200 watt units double the above primary amps consumed for the 600 watt power supply. Power Factor shall range from ≥0.98 / 115VAC, ≥0.95 230VAC, ≥0.93 / 277VAC. Secondary short circuit protection shall be automatic constant current limiting, recovering after fault condition is removed. Working Humidity rating shall be 20-95% RH non-condensing. Secondary terminal blocks shall be manufactured of UL 94VO rated UL class B 130°C compound. Terminal block shall have a service rating of, 85-amp, 600 volt, 125°c, rail mounted with elevator style wiring connection jaws.   All internal wiring shall be tin coated 125°C rated 600 volts. Cabinets shall be shiny un-sanded 304 stainless steel .039” gauge. Transformers shall be UL Listed, and CE listed for the purpose as per Underwrites Laboratory 2108 standard for safety. Transformer shall allow for the installation of optional 125-Watt 24 Volt DC power supply in cabinet of transformer to provide twenty-four-hour supply to CCTV camera systems if required. Contact Cast Lighting for details.  Transformer shall be plugged into a GFCI outlet or breaker during operation. GFCI Breaker is the preferred wiring method as it avoids potential field moisture conditions that may cause occasional unwanted nuisance tripping in the field mounted GFCI receptacle. Pigtail connections shall be molded SJTW style 105°C rated 62” in length, #16 gauge for 600-Watt units and #12 Gauge for 1200-Watt units. Power supply shall come with seven-year warranty.  Power supply shall be packaged in closed cell poly cell foam and cardboard box packaging for shipping to avoid damage to transformer. Using any non-approved power supply to operate any Cast Perimeter Luminaire voids all warranty.  As manufactured by Cast Lighting 1120- Goffle Road, Hawthorne NJ 07506 or approved equal.

- Ambient Operating Range Power Supply Capacity Rating:

-40 to +55C @85% Capacity (load all power supplies to 85% of capacity maximum)

- Power Supply Dimensions:

CPT600DCA, CPT1200DCA andCTP1200DCAI   Model   Height 17.5” (44.5cm) Width 13” (33cm) Depth 7” (18cm)

- Direct Sunlight / Adequate Ventilation / Shade

It is required that installation of power supply be placed in such a way that the cabinet is not in direct sunlight in arid desert condition and remains in northern exposure shade to prevent extreme heat buildup inside the cabinet under full sun. If power supply must be placed in direct sunlight provide a visor made of sheet metal, wood, composite, or other suitable material to provide shade for the power supply. If Transformer is to be placed in a Mild Steel Lockable enclosure installer must provide for venting of heat generated by power supply. It is recommended that venting fins of enclosure provide a bug screen to prevent infestation.

- Best practice for wiring secondary tap of Power Supply to field wires:

- Installer shall make a concerted effort to ensure no strands of the .010” multi strand wire are inadvertently cut during the installation process as this reduces the gauge of the wire and increases the resistance in the wiring and the overall watts consumed in the system leading to the needless increase in energy consumption and overall expense during the life of the system. Needlessly cutting strands of the .010” field wire also undermines the voltage delivery to luminaires and diminishes performance of the lighting system.

- Connections of the field wiring to the power supply tap must ensure no insulation remains on the stripped wire end that is placed in the elevator jaws of any secondary terminal block, as this will create a compromised wire connection and the resulting resistance in the connection will burn up the terminal block at power supply leading to system failure. All connections at power supply shall have only bare tin coated copper conductor in the elevator jaws of secondary tap terminal block. Installer shall firmly tighten all wire in elevator terminal block connections and tug on all installed wires afterwards and inspect to ensure a solid connection is made during installation and at final inspection. This is especially important when using large #10 and #8 Gauge wire.

  - LOW VOLTAGE LOW ENERGY CIRCUIT CABLE

Secondary low energy circuit cable shall be .010” stranded Cast No-Ox® Brand Tin Coated Marine Grade PVC insulated conductor. Construction consists of stranded annealed copper wire style SPT parallel with PVC insulation rated to 30Volts, black or grey in color PVC coating conforming to UL Class 43 to 60°C (140 F) thermoplastic, sunlight resistant, suitable for direct burial. One leg shall have a raised ridge for polarity. Operating range shall be 105°C (221 F) to -25°C (-13 F). Plain leg of wire shall read “Cast Lighting Size AWG XXXX 2/C Underground Low Energy Circuit Cable Sunlight Resistant for Outdoor Lighting (UL#)”. Wire shall be delivered in 500’ Put –Up roll and shall have printing on the wire in one-foot increments and identify a starting point of each roll at 500 feet and then sequentially decreasing to 1 foot in one-foot increments along entire wire length. As manufactured by Cast   Lighting 1120- Goffle Road, Hawthorne NJ 07506 or approved equal. Wire specifications per gauge and maximum operating amperage ratings shall be as shown in figure #10

  - ATTACHMENT OF WIRE TO TOP RAIL OF FENCE PIPE.

Should Installer choose to attach the Low Voltage No Ox Tin Coated Marine Grade Wire to the top rail of the fence, installer shall attach wire to pipe positioning wire at 7 O-Clock orientation and tightly secured in place to prevent wire movement in windy conditions using a ball lock flexible 304 stainless steel cable tie 350 Lbs. Tensile Strength, 11” Length, .310” Inch wide (7.96mm),  .010” thick (.23mm). Temperature rating -80C° to 538C°, UV Resistant as manufactured by Cast Lighting Part # CCT31011 or approved equal. Installer shall additionally install ¼” x 2” long heat shrink sleeving material over cable tie and place sleeving where cable tie rests over wire during installation to protect wire, as manufactured by Cast Lighting part number CHS1400 (100 ft Bulk Package).

Cable ties shall be placed 24inches (60cm) along fence rail to secure wire and directly at luminaire where wire enters and exits fixture. It is acceptable for installer to use UV resistant Nylon Cable ties to help stage wire during installation of the stainless wire ties. Do not remove UV ties after installation. Cut excess tie during installation.

2.09	LOW VOLTAGE LOW ENERGY LUMINAIRE SPLICE CONNECTIONS.

Electrical Connections at all luminaires shall use an approved outdoor weather resistant rated wire nut, insulated parallel crimp, or seamless insulated barrel crimp connection together with internal sealant heat shrink Polyolefin wire splice connection insulator. Each Fixture is provided with a cable piercing wire quick connect wire splice model# CPQC1 that works with #14, #12 & #10 Gauge No Ox Wire to connect Luminaire to power supply feed wire. Wire piercing quick connect wire splice eliminates accidental wire strand cutting that occurs when making a traditional wire nut or crimp connection field splice.  Installer shall take extra precaution when separating the two legs of conductor when attaching wire piercing quick connect wire splice so as not to cut the insulation and expose the bare conductor. Installer Shall use tile snip or similar tool to separate SPT wires along center separable seam as manufactured by Cast Lighting Model # C1098 Wire Splice / Wire separation Tool. For additional wire splice instructions contact Cast Lighting.

2.10    LOW VOLTAGE CABLE STRIPPING, INSULATION REMOVAL, COLD CONDITION.

Installer shall take caution not to cut any of the .010” tin coated wire strands contained in the wire / cable insulation jacket during luminaire installation or transformer terminal block secondary wiring, as this leads to increased resistance in the system wiring and will compromise system performance. Installer is advised to purchase IDEAL # 45-092 Strip Master wire insulation stripping tools, one fitted with # L-4419 blade set (02413) #8,10,12 Gauge and the other fitted with #L-4421 blade set ( 03813) #22,20,18,16,14,12,10 Gauge (www.idealindustries.com ) to insure proper insulation removal without damaging wire strands. In extreme cold (36°F or colder) conditions require warming up cable with electric heat gun prior to stripping wire which will make the PVC insulation more flexible and easier to work with in the field. In extreme cold (36°F or colder) wire must be kept at room temperature in a building then in a heated vehicle prior to despoiling wire to avoid potential insulation cracking during unspooling which will render the wire unusable.

2.11	ELECTRICAL GROUNDING:

As a safety measure and to minimize the damage to the perimeter security lighting system from any potential lightning strike on the fence line, metallic fence shall be separately earthed unless they come within 1.8 m of any equipment or structure above the surface of the ground, which is connected to the main earthing system. If the separation of 1.8 m cannot be obtained the fence shall be bonded to an earthing system as installed by qualified electrical contractor as follows or as per local electrical code.

## 2.11.1 Separately Earthed Fences

The earthing of a fence shall be provided by connecting certain metallic fence posts to an earth rod by a copper conductor. The earth rod shall be driven adjacent to the posts inside the fence line to a depth of not less than 8 foot (2.4 m). Where no metallic posts are provided the earth rods shall be connected directly to the metal wires, mesh or other components of the fence.

## 2.11.2 Earth Bonded Fences

Fences which need to be bonded to the main earthing system of the installation shall be connected by copper conductors to the nearest accessible point on the main earthing system. Bonds shall also be made to each corner post, at each gate and at intervals of not more than 330 feet (100m).

### Earth Bonding of Fence Components

2.11.2.a 	Fences made up of bolted steel or other metallic components do not require bonding between components. Where such fences have non-metallic components, bonds shall be installed to maintain continuity between metallic components. Reinforced concrete components shall be treated as being non-metallic.

2.11.2.b	Longitudinal wires for supporting other fence components or for anti-climbing guards and the wires of chain link shall be directly bonded to each fence earth electrode or to each bond to the main earthing system.

2.11.2.c		Wire fence components coated for anti-corrosion protection or PVC coated fence shall be earthed in accordance with this Clause.

### 2.11.3	Earth Bonding of Metallic Fencing Gates

The fixed metallic components on both sides of the gate shall be directly bonded together by a copper conductor installed under the surface of the access way. Flexible conductors shall be installed to bond the moving parts of the gates to the metallic fixed parts. An earth rod or a bond to the main earthing system shall be installed at each gate.

### 2.11.4	Earthing Conductors for Metallic Fences

All conductors used for earthing and bonding the fences and components and for outer rings shall have a cross-sectional area of not less than #4/0 / 185 mm2 copper.

Figure : 2.11 A   Plotted Resistance valueses

Figure :    2.11 B Typical Fence Grounding

3.00     INSTALLATION METHOD

Prior to installation installer must verify:

- Total Length of the fence line to be illuminated per zone

- If perimeter lighting system is to be integrated with third party intrusion detection system, the installation of NO or NC signal wire from command central location of the Intrusion detection system to the remote power supply zones (Model # CPT1200DCAI.) Different zones will require independent hard wired signal wires NO or NC to each zone from command central location of the Intrusion detection system. Other signal controls are available to communicate from the central control to the remote power supplies contact cast Lighting for Details.

- Total quantity of fixtures to be installed per zone.

- Gauge or Gauges of different cable to be used per zone including lead cable to first fixture (homerun feed cable gauge can be different in many cases to the rest of the fixtures in the run)

- Fixture spacing along fence line

- Verify voltage loss calculations to insure correct operating voltage of each luminaire.

3.01	POWER SUPPLY MOUNTING STAND TYPICAL

Power Supply installed remotely in a secure location using the method described in figure 11 is an acceptable mounting method in the absence of a building or remote structure to house transformer. In arid desert condition installer shall place power supply in northern exposure shade or provide alternate shade protection for power supply

Important Considerations for supplying primary power to remote power supply locations:

      - Installer shall provide adequate gauge primary power field wiring not to allow a voltage drop in excess of 15% from power source to remote power supply location during full load operation of the lighting system.

      - Primary power Installation methods and materials according to local electrical code.

      - Installer shall install dedicated electrical circuit breaker with GFI protection in the electrical panel, and identify circuit accordingly as “ Perimeter lights zone XXX ”

      - Installer shall include a “UL Rated Waterproof while in Use” electrical outlet enclosure cover for power supply field receptacle / plug connection as manufactured by Tay-Mac or approved Equal.

      - Secondary wires exiting power supply shall use conduit sized to quantity of wires exiting power supply. Install conduit to 10” below grade using 90’ electrical sweep at base.

3.02	MOUNTING POWER SUPPLY TO EXTERIOR OF BUILDING

When attaching Power Supply to block wall, concrete, wood, or brick surface use standard concrete anchor suitable for the material. Do NOT attach transformer on Vinyl Siding.  Follow items I-V above section 3.01 for additional information concerning primary power.

4.01

A.	LOW VOLTAGE WIRE INSTALLATION DIRECT BURIAL

All below grade direct burial wire installation shall adhere to local electric code. Typically, cable is direct buried at a depth of 6” below grade without the need for conduit according to NEC Code. Conduit installation is required under driveways, walks, dirt road, high traffic areas etc., at a 12” bury depth below grade. Consult Local code for acceptable installation methods.

4.01	B. 	ATTACHING LOW VOLTAGE WIRE TO FENCE FOR LUMINIERE WIRING

Low Voltage Power wire used to connect the fence mounted luminaire field wiring shall be attached to top fence pipe / rail positioned at 7 o clock and fastened using a stainless-steel ball lock cable tie 350 pound 11” .31 wide. Installer shall run cable tie thru a small 1/4” ID x 2” section of heat-shrink polyolefin material to protect cable tie as it rests against the conductor during installation. Place stainless cable ties 24” inches on center along fence rail. Cut excess Cable tie material when finished. Do not use UV rated Cable ties for wire attachment to fence as they will degrade and come apart in a short time although UV cable ties are acceptable wiring method to help stage the wire during installation of the stainless wire ties.

Many new fence systems now provide a pre-engineered cable tray feature embodied in the fence structure which allow for attachment of wire to the fence which does not require a cable tie. Contact fence manufacturer for specific details prior to commencing construction.

4.02 	LOW VOLTAGE CABLE INSTALLATION METHODS AT FENCE LOCATION

Many methods are available to an installer concerning field wiring using different materials and layouts to connect the power wire to the Luminaire installed on the fence, all of which are acceptable provided they follow common wiring techniques and adhere to local code and do not deviate from the voltage loss calculations and wire gauge selected for the system.

4.03    ATTACH FIXTURES TO FENCE POSTS AND POWER WIRE TO RAILS

  - TYPICAL SINGLE CONDUCTOR FIELD WIRING FIGURE 14

This method of field wiring is the most common as it provides for the fastest installation and the use of only one conductor to attach the luminaires to the power supply. Each Luminaire model consumes a different wattage and is limited to the distance they can operate.  This method does limit the distance you can run luminaires. (For greater distance with higher wattage luminaire models you need to use the STAGGERED LUMINAIRE WIRING METHOD in figure #15 which we will explain next paragraph 4.05)

For Single Wire Installation of Luminaires on Fence Line:

- The power supply is placed at the centermost position of the fence line of the lighting zone thus splitting the lighting zone into two equal quantities of fixtures on the left side and the right side of the zone. The left side luminaires will operate off circuit one of the power supply and the right-side luminaires will operate off circuit two of the power supply (example: zone XXX requires twenty-six fixtures model # CPL316 which will illuminate a fence line that is five hundred twenty feet long. Installer would split this zone in half leaving thirteen fixtures on the left side for circuit one and thirteen fixtures on the right side for circuit two operating on one transformer model CPT1200DCAI)

- Installer places the power supply as close to the fence as possible, as this reduces resistance in the wire and improves voltage delivery to the luminaires.

- This wiring method requires only one conduit be run up the fence post to feed both wires required for the left and right-side fixtures of circuit one and two.  To protect the two wires both are run up the fence post encased in a single liquid-tight, hard PVC (Poly Vinyl Chloride) or metal pipe conduit to the ½”(.860”)  knock out provided in the bottom plate junction box of either the first fixture on the left or right side wire run. Wire required for left or right-side fixtures exits conduit attached fixture by way of strain relief compression bottom plate opening provided in fixture.

- To facilitate final electrical testing contractor shall install a 6” (15cm) piece of # 18-2 wire at the first fixture and at the last fixture on each wire run. A voltage reading shall be taken with a True RMS voltage meter and recorded in transformer as built record label for future reference. Test Leads shall be capped off for future use.

  - 4.05    TYPICAL STAGGERED TWO WIRE FIELD WIRING. FIGURE 15

This method of field wiring provides for the furthest distance of light coverage and delivers the least voltage loss to power the luminaires resulting in the most uniform delivery of light. This requires the installation of two wires per right and left side spacing the fixtures forty feet apart on each wire with actual fixtures spaced twenty feet on center. Reference Figure # 15 for wiring diagram.

For Two Wire Staggered Method of Wire and Luminaires installation on Fence Line:

- The power supply is placed at the centermost position of the fence line of the lighting zone, breaking the lighting zone into two equal quantities of luminaires on the left side and the right side of the zone. The left side luminaires will operate off circuit one of the power supply and the right-side luminaires will operate off circuit two of the power supply.

- See staggered wiring example #15 page 26: In this example one zone requires thirty-eight fixtures model # CPL316 covering eight hundred feet of fence line. Splitting this zone in half would require nineteen luminaires left side circuit one, nineteen luminaires right side circuit two, with each luminaire spaced twenty feet on center.

- Installer places the power supply as close to the fence as possible, this reduces resistance in the wire and improves voltage delivery to the luminaires.

- To protect the two independent home run wires required to power the Left and Right-side luminaires, the two wires #10-2 for circuit #1 and the two #10-2 wires for circuit #2 are independently run up the fence post each encased in a liquid-tight, hard PVC (Poly Vinyl Chloride) or metal pipe conduit terminating in the first fixture using the ½” (.860”) conduit knock out in base of luminaire.

- Two independent wires are connected to circuit #1 and two independent wires are connected to circuit #2. One wire to power even numbered fixtures the second wire to power the odd numbered fixtures for both the left and right-side luminaires.

- To facilitate final electrical testing contractor shall install a 6” (15cm) piece of # 18-2 wire at the first fixture and at the last fixture on each wire run. A voltage reading shall be taken with a True RMS voltage meter and recorded in transformer as built record label for future reference. Test Leads shall be capped off for future use.

4.06	TYPICAL HIGH SECURITY FIELD WIRING

This method of field wiring involves trenching at the base of the secure interior of the fence and burying the cable 6” below grade or as required by Local or NEC electrical code. (Check local code prior to installation)

- Installer shall excavate wire trench using a chain trencher or other method to bury cable at a depth of 6” below grade along the inside of the fence line. Installer shall snake cable from side to side in trench to allow for expansion and contraction. Installer shall remove all large rocks and debris encountered during construction to provide a clean trench bed to place the wire in. Backfill with clean soil free of any stones greater than 1” inch and compact in several lifts to prevent settling. Remove all resulting waste rock and debris, rake clean and spread grass seed to excavated area or as instructed by owner.

- OTHER methods such as vibratory plough is acceptable however owner or owner’s representative must approve of cable burial method before commencing construction.

- Installer shall splice using a # 16-2 cable at each luminaire location to the buried below grade wire which shall serve to power fence mounted perimeter luminaires.

- Installer shall use non-insulated tin coated seamless butt crimp connection and pneumatic or ratcheting crimping tool to make secure electrical field cable crimp connections.

- Installer shall use direct burial polyolefin heat shrinkable wire insulation tubing with internal thermoplastic adhesive (inner liner) to provide a permanent flexible waterproof barrier for direct burial electrical splice connection. Heat shrinkable tubing shall have an operating range of -55°C (131 F) to 125°C (257 F) with a minimum heat shrink temperature of >110°C (230 F). Material shall meet ASTM D 2671 for heat shock, ASTM D 638 for heat aging, ASTM D 2671C for low temperature flexibility and UL 224 for flammability. As manufactured by Cast Lighting CLWS series crimp connection splice kits.

- All heat shrinking heat applications shall use only electric heat gun for applying heat to heat shrinkable tubing and under no circumstance shall an open flame or torch be used as this burns the material and causes failures over time.

- Heat shrink insulator shall fully collapsed over splice connection after applying heat and the surface of the polyolefin shall appear shiny and the internal clear sealant shall be visible at each end of the polyolefin heat shrink tubing when completed.

- Installer shall encase # 16-2 luminaire wire attaching to upright fence post  for all fixtures in liquid-tight, hard PVC (Poly Vinyl Chloride) or metal pipe conduit that extends a minimum of 6” below grade to protect wire from damage. Attach conduit using the ½” (.860”) knock out provided in the bottom plate junction box of Luminaire.

- Attach Conduit to upright fence post using hardware designed for the application and approved by the owner.

4.07	INTEGRAL FENCE POST WIRINNG SYSTEMS

Several manufacturers provide fence upright posts and horizontal structures that act as pre engineered cable conduit systems which are acceptable methods for providing power to perimeter lighting system.

5.01        ELECTRICAL SYSTEM TESTING AFTER INSTALLATION

- To facilitate final electrical testing contractor shall install a 6” (15cm) piece of # 18-2 wire at the first fixture and at the last fixture on each run. A voltage reading shall be taken with a True RMS voltage meter and recorded in power supply on the door label provided as built record label for future reference. Test Leads shall be capped off for future use.

- Optimal Operating Voltage of fixtures is between the range of 26 Volts and 17.0 Volts AC or  DC

- Installer shall use amperage gauge and test the full load amperage of power supply while system is operating to ensure power supply is not overloaded. Reference section 2.06 C for maximum amperage rating of power supply which can also be found on inside door of power supply.

- Contractor shall also take amperage rating of the secondary home run cable field wiring to ensure wire is not overloaded. (reference figure #10 section2.06)

- Contractor shall mark on the inside door of transformer with sharpie marker the following information:

  - Name of installer

  - Date of installation

  - Transformer Number

  - Voltage reading at first fixture on wire run.

  - Voltage reading at last fixtures at end of wire run.

  - Location of Primary Panel Breaker.

  - Operating Primary Voltage at the power supply under operating (Full Load) condition.

  - Operating Primary amperage of the power supply under operating (Full Load) condition

  - Amperage rating of each of the secondary wires (reference figure #10 section2.07)

5.02    FINAL ACCEPTANCE

- Initial Inspection: Installer shall operate the system for fourteen days dusk to dawn then schedule system inspection. During inspection installer shall set programs and demonstrate control devices and system functionality to the satisfaction of the owner or owner’s representative covering all items in 5.01.

- Any poorly installed luminaires, wires, conduit trenching compaction or cleanup shall be documented in a final punch list of items to be corrected and presented to installer for corrective action.

- Punch list items shall be corrected by installer within seven days weather permitting.

- Installer shall notify owner or owner’s representative of system completion and schedule a second inspection covering everything in punch list and covering again all items in 5.02. I.

Installation Details Figure   10  thru  15

Figure # 10

| Size | @80% of rated Capacity |
| --- | --- |
| AWG | Amps |
| 18 | 5 |
| 16 | 8 |
| 14 | 10 |
| 12 | 12 |
| 10 | 24 |
| 8 | 25 |

1 Transformer width required 15” inches (38.1CM)

Figure # 11

Figure # 12

FIGURE # 13

Figure # 14

Figure # 15

End